## Sheet2
|  | Round-trip wire length |  |  | 10 | feet
|  | Source voltage |  |  | 13 | V |  |  |  |  | No-loss current |  | 83.612 | A
|  | Inverter output |  |  | 1000 | W |  |  |  | Power at load |  |  | 1086.9565 | W
|  | Inverter efficiency |  |  | 92%
AWG | Metric | Wire Diameter |  | Resistivity |  | Round-trip Resistance | Voltage drop at source voltage (iteration 0) | Power loss in wire (iteration 0) | Current needed at applied voltage (iteration 1) | Voltage drop at source voltage (iteration 1) | Current needed at applied voltage (iteration 1) | Voltage drop at source voltage (iteration 2) | Current needed (iteration 2) | Voltage drop at source voltage (iteration 3) | Current needed (iteration 3) | Voltage drop at source voltage (iteration 4) | Current needed (iteration 4) | Voltage drop at source voltage (iteration 5) | Current needed (iteration 5) | Voltage drop at source voltage (iteration 6) | Current needed (iteration 6) | Voltage drop at source voltage (iteration 7) | Current needed (iteration 7) | Voltage drop at source voltage (iteration 8) | Current needed (iteration 8) | Voltage drop at source voltage (iteration 9) | Current needed (iteration 9) | Voltage drop at source voltage (iteration 10) | Current needed (iteration 10) | Voltage drop at source voltage (iteration 11) | Current needed (iteration 11) | Power Loss in Wire
| mm2 | inch | mm | ohm/1000' | ohm/km | ohms
24 | 0.205 | 0.0232 | 0.59 | 26.1823 | 85.9 | 0.26182 | 21.8916 | 1830.3976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
22 | 0.326 | 0.0293 | 0.744 | 16.4592 | 54 | 0.16459 | 13.7619 | 1150.6583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
20 | 0.518 | 0.0369 | 0.938 | 10.3632 | 34 | 0.10363 | 8.6649 | 724.4885 | 250.7329 | 25.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
18 | 0.823 | 0.0465 | 1.182 | 6.5227 | 21.4 | 0.065227 | 5.4538 | 456.0002 | 144.0395 | 9.3953 | 301.5359 | 19.6683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
16 | 1.309 | 0.0587 | 1.491 | 4.0843 | 13.4 | 0.040843 | 3.415 | 285.5323 | 113.4014 | 4.6317 | 129.8891 | 5.3051 | 141.256 | 5.7693 | 150.3256 | 6.1397 | 158.4427 | 6.4713 | 166.4883 | 6.7999 | 175.3122 | 7.1603 | 186.1315 | 7.6022 | 201.3691 | 8.2245 | 227.612 | 9.2964 | 293.483 | 11.9867 | 1072.7184 | FALSE | 0%
14 | 2.081 | 0.074 | 1.88 | 2.5756 | 8.45 | 0.025756 | 2.1535 | 180.0595 | 100.2128 | 2.5811 | 104.3253 | 2.687 | 105.3967 | 2.7146 | 105.6795 | 2.7219 | 105.7544 | 2.7238 | 105.7743 | 2.7243 | 105.7795 | 2.7245 | 105.7809 | 2.7245 | 105.7813 | 2.7245 | 105.7814 | 2.7245 | 105.7814 | 2.7245 | 105.7814 | 288.2022 | 26.51%
12 | 3.309 | 0.0933 | 2.371 | 1.6215 | 5.32 | 0.016215 | 1.3558 | 113.3586 | 93.3472 | 1.5136 | 94.6301 | 1.5344 | 94.8018 | 1.5372 | 94.8248 | 1.5376 | 94.8279 | 1.5376 | 94.8283 | 1.5376 | 94.8283 | 1.5376 | 94.8283 | 1.5376 | 94.8283 | 1.5376 | 94.8283 | 1.5376 | 94.8283 | 1.5376 | 94.8283 | 145.812 | 13.41%
10 | 5.261 | 0.1177 | 2.989 | 1.018 | 3.34 | 0.01018 | 0.85117 | 71.1681 | 89.4701 | 0.91081 | 89.9114 | 0.9153 | 89.9448 | 0.91564 | 89.9474 | 0.91566 | 89.9476 | 0.91567 | 89.9476 | 0.91567 | 89.9476 | 0.91567 | 89.9476 | 0.91567 | 89.9476 | 0.91567 | 89.9476 | 0.91567 | 89.9476 | 0.91567 | 89.9476 | 82.362 | 7.577%
8 | 8.366 | 0.1484 | 3.77 | 0.6401 | 2.1 | 0.006401 | 0.5352 | 44.7492 | 87.2021 | 0.55818 | 87.3631 | 0.55921 | 87.3704 | 0.55926 | 87.3707 | 0.55926 | 87.3707 | 0.55926 | 87.3707 | 0.55926 | 87.3707 | 0.55926 | 87.3707 | 0.55926 | 87.3707 | 0.55926 | 87.3707 | 0.55926 | 87.3707 | 0.55926 | 87.3707 | 48.863 | 4.495%
6 | 13.302 | 0.1871 | 4.753 | 0.4023 | 1.32 | 0.004023 | 0.33637 | 28.1247 | 85.8329 | 0.34531 | 85.8935 | 0.34555 | 85.8952 | 0.34556 | 85.8952 | 0.34556 | 85.8952 | 0.34556 | 85.8952 | 0.34556 | 85.8952 | 0.34556 | 85.8952 | 0.34556 | 85.8952 | 0.34556 | 85.8952 | 0.34556 | 85.8952 | 0.34556 | 85.8952 | 29.6817 | 2.731%
4 | 21.151 | 0.236 | 5.994 | 0.2533 | 0.831 | 0.002533 | 0.21179 | 17.7081 | 84.9968 | 0.2153 | 85.0201 | 0.21536 | 85.0205 | 0.21536 | 85.0205 | 0.21536 | 85.0205 | 0.21536 | 85.0205 | 0.21536 | 85.0205 | 0.21536 | 85.0205 | 0.21536 | 85.0205 | 0.21536 | 85.0205 | 0.21536 | 85.0205 | 0.21536 | 85.0205 | 18.3097 | 1.684%
2 | 33.631 | 0.2976 | 7.558 | 0.1594 | 0.523 | 0.001594 | 0.13328 | 11.1436 | 84.4781 | 0.13466 | 84.4872 | 0.13467 | 84.4873 | 0.13467 | 84.4873 | 0.13467 | 84.4873 | 0.13467 | 84.4873 | 0.13467 | 84.4873 | 0.13467 | 84.4873 | 0.13467 | 84.4873 | 0.13467 | 84.4873 | 0.13467 | 84.4873 | 0.13467 | 84.4873 | 11.3781 | 1.047%
1 | 42.408 | 0.3341 | 8.487 | 0.1265 | 0.415 | 0.001265 | 0.10577 | 8.8436 | 84.2979 | 0.10664 | 84.3036 | 0.10664 | 84.3036 | 0.10664 | 84.3036 | 0.10664 | 84.3036 | 0.10664 | 84.3036 | 0.10664 | 84.3036 | 0.10664 | 84.3036 | 0.10664 | 84.3036 | 0.10664 | 84.3036 | 0.10664 | 84.3036 | 0.10664 | 84.3036 | 8.9905 | 0.8271%
1/0 | 53.475 | 0.3752 | 9.53 | 0.1003 | 0.329 | 0.001003 | 0.083863 | 7.0119 | 84.1549 | 0.084407 | 84.1585 | 0.084411 | 84.1585 | 0.084411 | 84.1585 | 0.084411 | 84.1585 | 0.084411 | 84.1585 | 0.084411 | 84.1585 | 0.084411 | 84.1585 | 0.084411 | 84.1585 | 0.084411 | 84.1585 | 0.084411 | 84.1585 | 0.084411 | 84.1585 | 7.1039 | 0.6536%
2/0 | 67.431 | 0.4213 | 10.702 | 0.0796 | 0.261 | 0.000796 | 0.066555 | 5.5648 | 84.0423 | 0.066898 | 84.0445 | 0.066899 | 84.0445 | 0.066899 | 84.0445 | 0.066899 | 84.0445 | 0.066899 | 84.0445 | 0.066899 | 84.0445 | 0.066899 | 84.0445 | 0.066899 | 84.0445 | 0.066899 | 84.0445 | 0.066899 | 84.0445 | 0.066899 | 84.0445 | 5.6225 | 0.5173%
3/0 | 85.029 | 0.4732 | 12.018 | 0.0631 | 0.207 | 0.000631 | 0.052759 | 4.4113 | 83.9528 | 0.052974 | 83.9541 | 0.052975 | 83.9542 | 0.052975 | 83.9542 | 0.052975 | 83.9542 | 0.052975 | 83.9542 | 0.052975 | 83.9542 | 0.052975 | 83.9542 | 0.052975 | 83.9542 | 0.052975 | 83.9542 | 0.052975 | 83.9542 | 0.052975 | 83.9542 | 4.4475 | 0.4092%
4/0 | 107.219 | 0.5313 | 13.495 | 0.05 | 0.164 | 0.0005 | 0.041806 | 3.4955 | 83.8818 | 0.041941 | 83.8827 | 0.041941 | 83.8827 | 0.041941 | 83.8827 | 0.041941 | 83.8827 | 0.041941 | 83.8827 | 0.041941 | 83.8827 | 0.041941 | 83.8827 | 0.041941 | 83.8827 | 0.041941 | 83.8827 | 0.041941 | 83.8827 | 0.041941 | 83.8827 | 3.5182 | 0.3237%